SECTION 11135

SEWER PUMP STATION

- GENERAL

  - WORK INCLUDED

    - Refer to other applicable portions of these specifications for work indicated, but not specifically outlined in this section.

    - Furnish and install a complete factory built above ground duplex sewage pump system as indicated on the Plans and as described herein.

    - The Pump Station shall include two (2) self-priming suction lift centrifugal pumps with pump mounting plates with discharge piping, valves,  supports, precast concrete wet well, access hatch, level control system, electrical controls and appurtenances.

    - Design requirements consist of factory built pump station design, including materials of construction, pump features, valves and piping, and motor controls shall be in accordance with requirements listed under 2.0 PRODUCTS of this section.

    - Contractor shall furnish and install one (1) factory built above ground, automatic pump station. The station shall be complete with all equipment specified herein, factory assembled in a fiberglass reinforced polyester resin enclosure or other type enclosure as specified on the plans.  In addition to the station enclosure, principle items of equipment shall include two (2) horizontal, self-priming, centrifugal sewage pumps, V-belt drives, motors, internal piping, valves, motor control panel, automatic liquid level control system, and internal wiring.

  - PERFORMANCE CRITERIA

    - Pumps must be designed to handle raw, unscreened, domestic sanitary sewage.  Each pump shall be selected to perform under operating conditions as specified on the plans.

      - The operating conditions shall include the following parameters:

        - Capacity (GPM)

        - Total Dynamic Head (FT)

        - Total Dynamic Suction Lift (FT)

        - Maximum Repriming Lift (FT)

        - Maximum Static Suction Lift (FT)

        - Total Discharge Static Head (FT)

        - Minimum Submergence Depth (FT)

  - UTILITY POWER REQUIREMENTS

    - Site power furnished to pump station shall be as required by the pump manufacturer maintained within industry standards.  When available or can reasonably be extended to site, three (3) phase power shall be provided.

  - SUBMITTALS

    - Product Data

      - Contractor shall submit copies of submittal data for review and approval.

      - Submittal shall include shop drawings, electrical ladder logic drawings and support data as follows: Catalog cuts sheets reflecting characteristics for major items of equipment, materials of construction, major dimensions, motor and v-belt drive data, pump characteristic curves showing the design duty point capacity (GPM), head (FT), net positive suction head required (NPSHr) and hydraulic brake horsepower (BHP). Electrical components used in the motor branch and liquid level control shall be fully described.

    - Shop Drawings

      - Shop drawings shall provide layout of mechanical equipment and anchor bolt locations for station.

      - Pipe penetrations and station access clearances shall be dimensioned relative to the station centerline.

      - The electrical ladder logic drawings shall illustrate motor branch and liquid level control circuits to the extent necessary to validate function and integration of circuits to form a complete working system.

    - Operations and Maintenance Manuals

      - Operation shall be in accordance with written instructions provided by the pump station manufacturer. Comprehensive instructions supplied at time of shipment shall enable personnel to properly operate and maintain all equipment supplied. Content and instructions shall assume operating personnel are familiar with pumps, motors, piping and valves, but lack experience on exact equipment supplied.

      - Documentation shall be specific to the pump station supplied and collated in functional sections. Each section shall combine to form a complete system manual covering all aspects of equipment supplied by the station manufacturer. Support data for any equipment supplied by others, even if mounted or included in overall station design, shall be provided by those supplying the equipment. Instructions shall include the following as a minimum:

        - Functional description of each major component, complete with operating instructions.

        - Instructions for operating pumps and pump controls in all modes of operation.

        - Calibration and adjustment of equipment for initial start-up, replacement of level control components, or as required for routine maintenance.

        - Support data for commercially available components not produced by the station manufacturer, but supplied in accordance with the specifications, shall be supported by literature from the prime manufacturer and incorporated as appendices.

        - Electrical schematic diagram of the pump station circuits shall be in accordance with NFPA 70. Schematics shall illustrate, to the extent of authorized repair, pump motor branch, control and alarm system circuits including interconnections. Wire numbers and legend symbols shall be shown. Schematic diagrams for individual components, not normally repairable by the station operator, need not be included. Details for such parts shall not be substituted for an overall system schematic. Partial schematics, block diagrams, and simplified schematics shall not be provided in lieu of an overall system diagram.

        - Mechanical layout drawing of the pump station and components, prepared in accordance with good commercial practice, shall provide installation dimensions and location of all pumps, motors, valves and piping.

      - Operation and maintenance instructions which rely on vendor cut-sheets and literature which include general configurations, or require operating personnel to selectively read portions of the manual shall not be acceptable. Operation and maintenance instructions must be specific to equipment supplied in accordance with these specifications.

  - STANDARDS

    - Publications listed below form part of this specification to extent referenced in the text by basic designation only. Consult latest edition of publication unless otherwise noted.

    - American National Std. Institute (ANSI) &American Water Works Assoc. (AWWA)

      - ANSI B16.1 Cast iron pipe flanges and flanged fittings

      - ANSI/AWWA C115/A21.51 Cast/ductile iron pipe with threaded flanges

      - ANSI 253.1 Safety Color Code for Marking Physical Hazards

      - ANSI B40.1 Gages, Pressure and Vacuum

      - AWWA C508 Single Swing Check Valves

    - American Society for Testing and Materials (ASTM)

      - ASTM A48 Gray Iron Castings

      - ASTM A126 Valves, Flanges, and Pipe Fittings

      - ASTM A307 Carbon Steel Bolts and Studs

      - ASTM A36 Structural Steel

    - Institute of Electrical and Electronics Engineers (IEEE)

      - IEEE Std 100 Standard Dictionary of Electrical Terms

      - IEEE Std 112 Test Procedure for Polyphase Induction Motors

      - IEEE Std 242 Protection of Industrial and Control Power Systems

    - National Electric Code (NEC) / National Electrical Manufacturers’ Assoc. (NEMA)

      - NEC National Electrical Code

      - NEMA Std MG1 Motors and Generators

    - Miscellaneous References

      - Ten-State Standards Recommended Standards for Sewage Works

      - Hydraulic Institute Std for Centrifugal, Rotary and Reciprocating Pumps

      - ISO 9001 International Organization for Standardization

      - ISO 14001 International Organization for Standardization

  - QUALITY ASSURANCE

    - Manufacturer’s Qualifications

      - The pumps and pump station manufacturer must be ISO 9001:2008 revision certified, with scope of registration including design control and service after sales activities.

      - The pump station equipment specified in this section shall be furnished by and manufactured by Gorman Rupp.

      - The pumps and pump station manufacturer must be registered to the ISO 14001 Environmental Management System standard and as such is committed to minimizing the impact of its activities on the environment and promoting environmental sustainability by the use of best management practices, technological advances, promoting environmental awareness and continual improvement.

      - Upon request from the Engineer, the pump station manufacturer shall prove financial stability and ability to produce the station within the specified delivery schedules. Evidence of facilities, equipment and expertise shall demonstrate the manufacturer's commitment to long term customer service and product support.

      - Manufacturer must show proof of original product design and testing.  Products violating intellectual property regulations shall not be allowed, as they may violate international law and expose the user or Engineer to unintended liabilities.  “Reverse-engineered” products fabricated to substantially duplicate the design of original product shall not be allowed, as they may contain substantial differences in tolerances and material applications addressed in the original design, which may contribute to product failure.

      - The term “pump manufacturer” or “pump station manufacturer” shall be defined as the entity which designs, machines, assembles, hydraulically tests and warranties the final product.  Any entity that does not meet this definition will not be considered a “pump manufacturer” or “pump station manufacturer” and is not an acceptable supplier.  For quality control reasons and future pump and parts availability, all major castings of the pump shall be sourced and machined in North America.

    - Pump Performance Certifications

      - Solids Management System

        - A designed system for grinding/management of sanitary wipes, plastic bags, feathers, hair, sludge, and all other types of stringy solids.

      - Solids Handling Capability

        - All internal passages, impeller vanes and recirculation ports shall pass a 2.5 inch spherical solid. Smaller internal passages that create a maintenance nuisance or interfere with priming and pump performance shall not be permitted. Upon request from the Engineer, manufacturer’s certified drawings showing size and location of the recirculation port(s) shall be submitted for approval.

      - Reprime Performance

        - Consideration shall be given to the sanitary sewage service anticipated, in which debris is expected to lodge between the suction check valve and its seat, resulting in the loss of the pump suction leg, and siphoning of liquid from the pump casing to the approximate center line of the impeller. Such occurrence shall be considered normal and the pump must be capable of automatic, unattended operation with an air release line installed.

        - During unattended operation, the pump shall retain adequate liquid in the casing to insure automatic repriming while operating at its rated speed in a completely open system. The need for a suction check valve or external priming device shall not be required.

        - Pump must reprime 9.0 vertical feet at the specified speed and impeller diameter. Reprime lift is defined as the static height of the pump suction above the liquid, while operating with only one-half of the liquid remaining in the pump casing. The pump must reprime and deliver full capacity within five (5) minutes after the pump is energized in the reprime condition. Reprime performance must be confirmed with the following test set-up:

        - A check valve to be installed downstream from the pump discharge flange. The check valve size shall be equal (or greater than) the pump discharge diameter.

        - A length of air release pipe shall be installed between pump and the discharge check valve.  This line shall be open to atmosphere at all times duplicating the air displacement rate anticipated at a typical pump station fitted with an air release valve.

        - The pump suction check valve shall be removed. No restrictions in the pump or suction piping will prevent the siphon drop of the suction leg. Suction pipe configuration for reprime test shall incorporate a two (2) feet minimum horizontal run, a 90 degree elbow and vertical run at the specified lift. Pipe size shall be equal to the pump suction diameter.

        - Impeller clearances shall be set as recommended in the pump service manual.

        - Repeatability of performance shall be demonstrated by testing five (5) consecutive reprime cycles. Full pump capacity (flow) shall be achieved within five (5) minutes during each cycle.

        - Liquid to be used for reprime test shall be water.

        - Upon request from the Engineer, certified reprime performance test results, prepared by the manufacturer, and certified by a registered professional Engineer, shall be prepared and forwarded to the customer.

    - Certified Pump Performance Test

      - Tests shall be conducted in accordance with Hydraulic Institute Standards 14.6.3.4 Acceptance Grade 2B at the specified head, capacity, rated speed and horsepower.  The performance tests will validate the correct performance of the equipment at the design head, capacity and speed.

      - Tests shall be conducted in accordance with Hydraulic Institute Standards at the specified head, capacity, rated speed and horsepower.

    - Factory System Test

      - All internal components including the pumps, motors, valves, piping and controls will be tested as a complete working system at the manufacturer's facility. Tests shall be conducted in accordance with Hydraulic Institute Standards at the specified head, capacity, rated speed and horsepower. Factory operational test shall simulate actual performance anticipated for the complete station.

      - Upon request from the Engineer, the operational test may be witnessed by the engineer, and/or representatives of his choice, at the manufacturer's facility.

  - MANUFACTURER’S WARRANTY

    - The pump station manufacturer shall warrant all equipment to be of quality construction, free of defects in material and workmanship. A written warranty shall include specific details described below.

    - In addition to defects in material and workmanship, fiberglass reinforced polyester station enclosures are warranted for 60 months to be resistant to rust, corrosion, corrosive soils, effects of airborne contamination or physical failures occurring in normal service for the period of the pump station warranty.

    - All other equipment, apparatus, and parts furnished shall be warranted for 60 months, excepting only those items that are normally consumed in service, such as light bulbs, oils, grease, packing, gaskets, O-rings, etc. The pump station manufacturer shall be solely responsible for warranty of the station and all components.

    - Components failing to perform as specified by the Engineer, or as represented by the manufacturer, or as proven defective in service during the warranty period, shall be replaced, repaired or satisfactorily modified by the manufacturer.

    - It is not intended that the station manufacturer assume liability for consequential damages or contingent liabilities arising from failure of any vendor supplied product or part which fails to properly operate, however caused. Consequential damages resulting from defects in design, or delays in delivery are also beyond the manufacturer's scope of liability.

    - Equipment supplied by others and incorporated into a pump station or enclosure is not covered by this limited warranty. Any warranty applicable to equipment selected or supplied by others will be limited solely to the warranty, if any, provided by the manufacturer of the equipment.

    - This limited warranty shall be valid only when installation is made and use and maintenance is performed in accordance with manufacturer recommendations. A start-up report competed by an authorized manufacturer’s representative must be received by manufacturer within 30 days of the initial date the unit is placed into service. The warranty shall become effective on the date of acceptance by the purchaser or the purchaser's authorized agent, or 60 days after installation, or 90 days after shipment from the factory, whichever occurs first.

- PRODUCTS

  - UNITARY RESPONSIBILITY

    - In order to unify responsibility for proper operation of the complete pumping station, it is the intent of these Specifications that all system components be furnished by a single supplier (unitary source). The pumping station must be of standard catalog design and totally warranted by the manufacturer. Under no circumstances will a system consisting of parts compiled and assembled by a manufacturer's representative or distributor be accepted.

  - MANUFACTURER

    - The pump station system integrator must be ISO 9001:2000 revision certified, with scope of registration including design control and service after sales activities.

  - STATION ENCLOSURE

    - This section is for enclosures provided by the pump manufacturer.  In some cases, the PSA may call for the enclosure to be provided by others or designed specifically by the Engineer.  In such cases, the specific design is to be coordinated with the PSA.

    - The station enclosure shall contain and protect all pumps, interior piping, valves and associated controls. Enclosure shall incorporate the following design and service features:

      - Access panels must be supplied on all sides. Location and size shall permit access for routine maintenance functions such as pump and motor inspection, drive belt adjustment and pump clean out. Non-hinged panels shall be secured with stainless steel tamper-proof hardware.

      - A continuous hinge and latch shall be installed on at least two (2) access panels. The hinged panels shall allow easy access to the electrical controls for frequent adjustments and inspections. A two-point mechanical latch assembly shall secure the panel at top and bottom. Latch handle locks shall be match keyed, requiring only one (1) key to open all access panels.

      - A vent in one (1) access panel shall allow free air flow for enclosure ventilation.

      - The complete station enclosure, less base, must be completely removable after disengaging reusable hardware. After disassembly, no portion of the enclosure (except electrical service entrance) shall project above the base surface to interfere with maintenance or endanger personnel.

      - Disassembly and removal of the enclosure shall require no more than two (2) people working without assistance of lifting equipment.

    - Station enclosure shall be manufactured of molded reinforced orthophthalic polyester resins with a minimum of 30% fiberglass, and a maximum of 70% resin. Resin fillers or extenders shall not be used.

    - Chopped glass fibers of 1 1/4 inch average length shall be sprayed and rolled. Major design consideration shall be given to structural stability, corrosion resistance, and watertight integrity. The polyester laminates shall provide a balance of mechanical, chemical and electrical properties to insure long life. They must be impervious to micro-organisms, mildew, mold, fungus, corrosive liquids and gases which are expected to be present in the environment surrounding the wet well.

    - All interior surfaces of the housing shall be coated with a polyester resin-rich finish providing maintenance-free service, abrasion resistance, and protection from sewage, greases, oils, gasoline and other common chemicals.

    - Outside surfaces of the enclosure shall be coated with gel-coat pigmented resin to insure long maintenance-free life and UV protection. Color used shall de-emphasize the presence of dirt, grease, etc.

    - Station base shall be constructed of pre-cast, reinforced concrete encapsulated in a fiberglass mold. The design shall resist deformation of the structure during shipping, lifting or handling. Base shall incorporate drainage provisions and an opening sized to permit installation of piping and service connections to the wet well. After installation, the opening shall serve as a grout dam to be utilized by the contractor. The base shall incorporate anchor bolt recesses for securing the complete station to a concrete pad (supplied by the contractor) in accordance with the project plans.

    - A blower mounted in the station roof shall be sized to exchange station air volume at least once every two (2) minutes. Blower motor shall energize automatically at approximately 70 degrees F, and turn off at 55 degrees F. The blower motor control circuit shall incorporate a thermal-magnetic circuit breaker providing overcurrent and overload protection. Exhaust and inlet locations shall prevent the entrance of rain, snow, or debris.

  - STATION HEATER

    - Pump station shall be provided with a 1300/1500 watt, 115 volt electric heater with cord and grounding plug. Ungrounded heaters shall not be acceptable.

  - INSULATION PACKAGE

    - The pump station shall be furnished with one (1) inch thick spray foam insulation, which shall be applied to the roof, doors, and corner panels.

  - DOOR OPEN NOTIFICATION

    - The station enclosure shall include limit switches with defeater switch alarm circuit and time delay, mounted and wired in the station enclosure to indicate that there has been a door left open or unauthorized entry to the station. There shall be an adjustable time period for the operator to disable alarm with an unmarked pushbutton located inside the station. The notification shall be activated when a station door or access panel is opened. Includes dry contacts pre-wired to a terminal strip for remote monitoring.

  - HAND LAMP

    - Pump station shall be provided with a 100 watt, 115 volt AC vapor-tight hand lamp with 25 feet of cord and grounding plug.  Hand lamp shall be constructed of corrosion resistant materials, and shall be equipped with a guard and a clear globe.  Ungrounded hand lamps may be supplied if provided with an effective means of double insulation.

  - PUMP DESIGN

    - Pump shall be horizontal, self-priming centrifugal type, designed specifically for handling raw unscreened domestic sanitary sewage or industrial waste. Pump solids handling capability and performance criteria shall be in accordance with requirements listed under Part 1 - General of this Section.

    - The pump manufacturer must be ISO 9001:2000 revision certified, with scope of registration including design control and service after sales activities.

  - MATERIALS AND CONSTRUCTION FEATURES

    - Pump casing shall be cast iron Class 30 with integral volute scroll. Casing shall incorporate following features:

      - Mounting feet sized to prevent tipping or binding when pump is completely disassembled for maintenance.

      - Fill port cover plate, 3 1/2 inch diameter, shall be opened after loosening a positive lock clamp bar assembly. In consideration for safety, capscrew threads must provide slow release of pressure, and the clamp bar shall be retained by detente lugs. A non-metallic gasket shall prevent adhesion of the fill port cover to the casing while assuring a reliable seal.

      - Casing drain plug shall be at least 1 1/4 inch NPT to insure complete and rapid draining.

      - Liquid volume and recirculation port design shall be consistent with performance criteria listed under Part 1 - General of this Section.

    - Coverplate assembly shall be cast iron Class 30. Design must incorporate following maintenance features:

      - A lightweight inspection coverplate, retained by acorn nuts, for access to pump interior for removal of stoppages.  Designs that require removal of complete coverplate assembly for access to the impeller will not be accepted.

      - Retained by acorn nuts for complete access to pump interior. Back coverplate removal must allow service to the impeller, seal, wear plate or check valve without removing suction or discharge piping.  Back coverplate shall incorporate an obstruction free flow path by combining four support posts into a two-point “webbed” plate design for increased durability, reduced clogging, and increased operational efficiency.

      - Aggressive Self-Cleaning Wear Plate

        - A replaceable wear plate secured to the back cover plate by studs and nuts.   Wear plate shall be self-cleaning design ensuring that debris is cleared away and does not collect on the impeller vanes.

        - The nature of the conveyed medium poses significant challenges to the continuous operation of the pump.  Of particular concern is the clogging of the impeller by debris in the pumped medium including but not limited to long rags, fibers, and like debris which are able to wrap around the impeller vanes, stick to the center of the vanes or hub, or lodge within the spaces between the impeller and the housing.

        - The aggressive self-cleaning wear plate shall have integral laser cut notches and grooves in combination with a “tooth” designed to disturb and dislodge any solids which might otherwise remain on the impeller in dynamic operation.  Wear plate is designed to constantly and effectively clear the eye of the impeller without the use of blades or cutters.

      - In consideration for safety, a pressure relief valve shall be supplied in the inspection coverplate. Relief valve shall open at 75-200 PSI.

      - One O-ring of Buna-N material shall seal inspection coverplate to back coverplate.

      - Two O-rings of Buna-N material shall seal back coverplate to pump casing.

      - Pusher bolt capability to assist in removal of inspection coverplate or back coverplate. Pusher bolt threaded holes shall be sized to accept same retaining capscrews as used in rotating assembly.

      - Easy-grip handle shall be mounted to face of inspection coverplate.

    - Rotating assembly, which includes impeller, shaft, mechanical shaft seal, lip seals, bearings, seal plate and bearing housing, must be removable as a single unit without disturbing the pump casing or piping. Design shall incorporate the following features:

      - Seal plate and bearing housing shall be cast iron Class 30. Anti-rotation ribs shall be cast into the sealplate to reduce internal wear and maximize component life. Separate oil filled cavities, vented to atmosphere, shall be provided for shaft seal and bearings. Cavities must be cooled by the liquid pumped. Three (3) lip seals will prevent leakage of oil.

        - The bearing cavity shall have an oil level sight gauge and fill plug check valve. The clear sight gauge shall provide easy monitoring of the bearing cavity oil level and condition of oil without removal of the fill plug check valve. The check valve shall vent the cavity but prevent introduction of moist air to the bearings.

        - The seal cavity shall have an oil level sight gauge and fill/vent plug. The clear sight gauge shall provide easy monitoring of the seal cavity oil level and condition of oil without removal of the fill/vent plug.

        - Double lip seal shall provide an atmospheric path providing positive protection of bearings, with capability for external drainage monitoring.

      - Impeller shall be ductile iron (unless other material is specifically called for by the PSA upon recommendation by the pump manufacturer), two (2) vane, semi-open, non-clog, with integral pump out vanes on the back shroud. Impeller shall be statically or dynamically balanced. Impeller shall thread onto the pump shaft and be secured with a lockscrew and conical washer.

      - Shaft shall be AISI 4140 alloy steel unless otherwise specified by the Engineer or PSA upon recommendation of the pump manufacturer, in which case AISI 17-4 pH stainless steel shall be supplied.

      - Bearings shall be anti-friction ball type of proper size and design to withstand all radial and thrust loads expected during normal operation. Bearings shall be oil lubricated from a dedicated reservoir. Pump designs which use the same oil to lubricate the bearings and shaft seal shall not be acceptable.

      - Shaft seal shall be oil lubricated mechanical type. The stationary and rotating seal faces shall be silicon carbide alloy. Each mating surface shall be lapped to within three (3) light bands flatness (35 millionths of an inch), as measured by an optical flat under monochromatic light. The stationary seal seat shall be double floating by virtue of a dual O-ring design. An external O-ring secures the stationary seat to the sealplate, and an internal O-ring holds the faces in alignment during periods of mechanical or hydraulic shock (loads which cause shaft deflection, vibration, and axial/radial movement). Elastomers shall be viton; cage and spring to be stainless steel. Seal shall be oil lubricated from a dedicated reservoir. The same oil shall not lubricate both shaft seal and shaft bearings. Seal shall be warranted in accordance with requirements listed under Part 1 - General of this Section.

      - Pusher bolt capability to assist in removal of rotating assembly. Pusher bolt threaded holes shall be sized to accept same capscrews as used for retaining rotating assembly.

      - Self-cleaning wear plate features shall be included in the design to constantly and effectively clear the eye of the impeller.

    - Adjustment of the impeller face clearance (distance between impeller and wearplate) shall be accomplished by external means.

      - Clearances shall be maintained by a four-point external shimless coverplate adjustment system, utilizing a four-collar and four (4) adjusting screw design allowing for incremental adjustment of clearances by hand as required. Each of the four (4) points shall be lockable to prevent inadvertent clearance increases or decreases due to equipment vibration or accidental operator contact.  The four (4) point system also allows for equal clearance gaps at all points between the impeller and wear plate. Requirement of realignment of belts, couplings, etc., shall not be acceptable. Coverplate shall be capable of being removed without disturbing clearance settings. Clearance adjustment systems that utilize less than four (4) points will not be considered.

      - There shall be provisions for additional clearance adjustment in the event that adjustment tolerances have been depleted from the coverplate side of the pump. The removal of stainless steel tabbed spacers from the rotating assembly side of the pump shall allow for further adjustment as described above.

      - Clearance adjustment which requires movement of the shaft only, thereby adversely affecting seal working length or impeller back clearance, shall not be acceptable.

    - An externally removable suction check valve shall be molded neoprene with integral steel and nylon reinforcement. A blow-out center shall protect pump casing from hydraulic shock or excessive pressure. Removal or installation of the check valve must be accomplished from the top of pump without disturbing the suction piping or completely draining the casing. Sole function of check valve shall be to save energy by eliminating need to reprime after each pumping cycle. Pumps requiring a suction check valve to assist reprime will not be acceptable.

    - Pump shall include flange kit consisting of two (2) female 125# NPT cast iron class 30 flanges suitable for attachment to suction and discharge ports.

  - SERVICEABILITY

    - The pump manufacturer shall demonstrate to the Engineer's satisfaction that consideration has been given to reducing maintenance costs.

    - No special tools shall be required for replacement of any components within the pump.

  - SPARE PARTS KIT

    - The following minimum spare parts shall be furnished with the pump station:

      - One (1) pump mechanical seal

      - Required cover plate O-Ring(s)

      - One (1) rotating assembly O-Ring(s)

      - One (1) set of impeller clearance adjustment spacers

      - One (1) complete rotating assembly

  - VALVES AND PIPING

    - Check Valve

      - Each pump shall be equipped with a full flow type check valve capable of passing a three (3) inches spherical solid.

      - Valve shall be constructed with flanged ends and fitted with an external lever and torsional spring.

      - Valve seat shall be constructed of stainless steel, secured to the body to ensure concentricity, sealed by an O-ring, and shall be replaceable.

      - The valve body shall be cast iron incorporating a clean-out port large enough to allow removal and/or replacement of the valve clapper without removing valve or piping from the line.

      - Valve clapper shall have a molded neoprene seating surface incorporating low pressure sealing rings.

      - Valve hinge pin and internal hinge arm shall be stainless steel supported on each end in brass bushings.

      - Shaft nut shall have double O-rings which shall be easily replaceable without requiring access to interior of valve body.

      - All internal hardware shall be stainless steel.

      - Valve shall be rated at 175 psi water working pressure, 350 psi hydrostatic test pressure.

      - Valves other than full flow type or valves mounted in such a manner that prevents the passage of a three (3) inches spherical solid shall not be acceptable.

    - Plug Valve

      - A 3-way plug valve must allow either or both pumps to be isolated from the force main.

      - The plug valve shall be non-lubricated, tapered type.

      - Valve body shall be cast iron with flanged end connections drilled to 125 pound standard.

      - The drip-tight shutoff plug shall be mounted in stainless steel bearings and shall have a resilient facing bonded to the sealing surface.

      - Valve shall be operated with a single lever actuator providing lift, turn and reseat action.

      - The lever shall have a locking device to hold the plug in the desired position.

    - Automatic air release valves:

      - An automatic air release valve shall be furnished for each pump designed to permit the escape of air to the atmosphere during initial priming or unattended repriming cycles.  Upon completion of the priming cycle or repriming cycle, the valve shall close to prevent recirculation.  Valves shall provide visual indication of valve closure, and shall operate solely on discharge pressure.  Valves which require connection to the suction line shall not be acceptable.

      - All valve parts exposed to sewage shall be constructed of cast iron, stainless steel or similar corrosion resistant materials.  Diaphragms, if used, shall be of fabric-reinforced neoprene or similar inert material.

      - A cleanout port, three (3) inches in diameter, shall be provided for ease of inspection, cleanout and service.

      - Valves shall be field adjustable for varying discharge heads.

      - Connection of the air release valves to the station piping shall include stainless steel fittings.

    - Gauge Kit

      - A gauge kit shall be supplied for each pump. Suction pressure must be monitored by a glycerin-filled compound gauge, and discharge pressure by a glycerin-filled pressure gauge. Gauges to be at least four (4) inches in diameter, graduated in feet water column. Rated accuracy shall be one (1) percent of full scale reading. Compound gauge shall be graduated -34 to +34 feet water column minimum. Pressure gauge to be graduated zero to 140 feet water column minimum.

      - Gauges to be factory mounted on a resilient panel with frame assembly secured to pumps or piping. Gauge installations shall be complete with all hoses and stainless steel fittings, including a shutoff valve for each gauge line at the point of connection to suction and discharge pipes.

  - STATION ENCLOSURE LOW TEMPERATURE ALARM

    - Pump station shall be supplied with a thermostat which shall monitor interior station temperature. The control shall incorporate an unpowered dry contact wired to terminal blocks for field connection to a remote alarm device. The contact will close in the event that the temperature within the enclosure falls below approximately 35 degrees F.

  - PIPING

    - Flanged header pipe shall be centrifugally cast, ductile iron, complying with ANSI/AWWA A21.51/C115 and class 53 thickness.

    - Flanges shall be cast iron class 125 and Comply with ANSI B16.1.

    - Pipe and flanges shall be threaded and suitable thread sealant applied before assembling flange to pipe.

    - Bolt holes shall be in angular alignment within 1/2 degree between flanges. Flanges shall be faced with a gasket finish having concentric grooves a minimum of 0.01 inch deep by approximately 0.03 inch wide, with a minimum of three (3) grooves on any given surface spaced a maximum of 1/4 inch apart.

    - Supports and Thrust Blocking

      - Contractor must insure all pipes connected to the pump station are supported to prevent piping loads from being transmitted to pumps or station piping. Pump station discharge force main piping shall be anchored with thrust blocks and/or joint restraints where shown on the contract drawings.

  - PORTABLE PUMP DISCHARGE CONNECTION

    - The station header pipe shall incorporate a 2-way plug valve to permit emergency access to the pump station force main after isolation of the pumps. Valve body shall be cast iron with flanged end connections drilled to 125 pound standard. The plug valve shall be non-lubricated type, furnished with a drip-tight shutoff plug mounted in stainless steel or Teflon over phenolic bearings, and shall have a resilient facing bonded to the sealing surface.

    - When enclosure is provided by pump manufacturer, the bypass connection shall be accessible behind the hinged access panel on the wet well side of the station enclosure and shall terminate with a male OPW type quick connect fitting.

  - DRIVE UNIT

    - Motors

      - Pump motors shall be 60 Hz, horizontal ODP, NEMA rated with cast iron frame with copper windings, induction type, with class F insulation and 1.15 Service Factor for normal starting torque and low starting current characteristics, suitable for continuous service. The motors shall be sized to not overload at the design condition or at any head in the operating range as specified. Motors shall be suitable for operation using the utility power available.

      - Motors shall be tested in accordance with provisions of ANSI/IEEE Std. 112, Method B.

  - DRIVE TRANSMISSION

    - Power to pumps transmitted V-belt drive assemblies. The sheave/belt combination shall provide the speed ratio needed to achieve the specified pump operating conditions.

    - Each drive assembly shall utilize at least two (2) V-belts providing minimum a combined safety factor of 1.5. Single belt drives or systems with a safety factor of less than 1.5 are not acceptable. Computation of safety factors shall be based on performance data published by the drive manufacturer.

    - Precise alignment tolerances of the drive assemblies shall be achieved by means of a belt/sheave laser alignment system resulting in the reduction of vibration, accelerated wear and premature failure.

    - The pump manufacturer shall submit power transmission calculations which document the following:

      - Ratio of pump/motor speed.

      - Pitch diameter of driver and driven sheaves.

      - Number of belts required per drive.

      - Theoretical horsepower transmitted per belt, based on vendor's data.

      - Center distance between pump and motor shafts.

      - Arc-length correction factor applied to theoretical horsepower transmitted.

      - Service factor applied to established design horsepower.

      - Safety factor ratio of power transmitted/brake horsepower required.

    - Pump drives to be enclosed on all sides by a guard constructed of fabricated steel or combination of materials including expanded, perforated, or solid sheet metal. No opening to a rotating member shall exceed 1/2 inch.

      - Guards must be completely removal without interference from any unit component, and shall be securely fastened and braced to the unit base.

      - Metal to be free from burrs and sharp edges. Structural joints shall be continuously welded. Rivet spacing on panels shall not exceed five (5) inches. Tack welds shall not exceed four (4) inch spacing.

      - The guard shall be finished with one (1) coat of gray W.R. non-lift primer and one coat of orange acrylic alkyd W.R. enamel in accordance with Section 3, Color Definitions of ANSI 253.1; Safety Color Code for Marking Physical Hazards.

  - FINISH

    - Pumps, piping, and exposed steel framework shall be cleaned prior to painting.  Exposed surfaces to be coated with one (1) coat gray W.R. non-lift primer and one (1) coat white acrylic alkyd W.R. enamel. Paint shall be low VOC, alkyd based, high solids, semi-gloss white enamel for optimum illumination enhancement, incorporating rust inhibitive additives.  The finish coat shall be 1.0 to 1.2 MIL dry film thickness (minimum), resistant to oil mist exposure, solvent contact and salt spray.  The factory finish shall allow for over-coating and touch up after final installation.

  - ELECTRICAL CONTROL COMPONENTS

    - The pump station control panel will be tested as an integral unit by the pump station manufacturer. The control panel shall also be tested with the pump station as a complete working system at the pump station manufacturer's facility.

  - PANEL ENCLOSURE

    - Electrical control equipment shall be mounted within a common NEMA 1 stainless steel, dead front type control enclosures. Doors shall be hinged and sealed with a neoprene gasket and equipped with captive closing hardware. Control components shall be mounted on removable steel back panels secured to enclosure with collar studs.

    - All control devices and instruments shall be secured to the sub-plate with machine screws and lockwashers. Mounting holes shall be drilled and tapped; self-tapping screws shall not be used to mount and component. All control devices shall be clearly labeled to indicate function.

  - UL LABEL REQUIREMENT

    - Pump station controls shall conform to third party safety certification. The panel shall bear a serialized UL label listed for "Enclosed Industrial Control Panels". The enclosure, and all components mounted on the sub-panel or control cover, shall conform to UL descriptions and procedures.

  - BRANCH COMPONENTS

    - All motor branch and power circuit components shall be of highest industrial quality. The short circuit current rating of all power circuit devices shall be a tested combination or evaluated per the National Electrical Code Article 409. The lowest rated power circuit component shall be the overall control panel short circuit rating and shall not be less than the fault current available. The minimum control panel rating shall not be less than 10 kA, rms symmetrical.  Control assemblies operating at 120 volts nominal or less may be provided with transformers which limit the fault current and may be rated less than the minimum required short circuit rating.

    - Circuit Breakers and Operating Mechanisms

      - A properly sized heavy duty circuit breaker shall be furnished for each pump motor. The circuit breakers must be sealed by the manufacturer after calibration to prevent tampering.

      - An operating mechanism installed on each motor circuit breaker shall penetrate the control panel door. A padlockable operator handle shall be secured on the exterior surface. Interlocks must prevent opening the door until circuit breakers are in "OFF" position.  An additional mechanism(s) shall be provided on the circuit breaker permitting the breaker to be operated and/or locked with the control panel door in the open position.

    - Motor Starters

      - An open frame, across-the-line, NEMA rated magnetic starter with under-voltage release, and overload protection on all three (3) phases, shall be furnished for each pump motor. Starters of NEMA size 1 and above shall allow addition of at least two (2) auxiliary contacts. Starters rated "O", "OO", or fractional size are not acceptable. Power contacts are to be double-break type made of cadmium oxide silver. Coils are to be epoxy molded for protection from moisture and corrosive atmospheres. Contacts and coils shall be easily replaceable without removing the starter from its mounted position. Each starter shall have a metal mounting plate for durability.

    - Overload Relays

      - Overload relays shall be solid-state block type, having visual trip indication with trip-free operation.  Electrically resetting the overload will cause one (1) normally open and one (1) normally closed isolated alarm/control contact to reset, thus re-establishing a control circuit. Trip setting shall be governed by solid-state circuitry and adjustable current setting. Trip classes shall be 10, 15 and 20. Additional features to include phase loss protection, selectable jam/stall protection and selectable ground fault protection.

      - A reset pushbutton, mounted through the control panel door, shall permit resetting the overload relays without opening the door.

    - Phase Monitor – Three Phase Power

      - The control panel shall be equipped to monitor the incoming power and shut down the pump motors when required to protect the motor(s) from damage caused by phase reversal, phase loss, voltage unbalance, high voltage, and low voltage. An adjustable time delay shall be provided to minimize nuisance trips. The motor(s) shall automatically restart, following an adjustable time delay, when power conditions return to normal.

    - Phase Monitor – Single Phase Power

      - The control panel shall be equipped to monitor the incoming power and shut down the pump when required to protect the motor(s) from damage caused by voltage less than 83% of nominal. The motor(s) shall automatically restart when power conditions return to normal.

    - Transient Voltage Surge Suppressor

      - The control panel shall be equipped with a transient voltage surge suppressor to minimize damage to the pump motors and control from transient voltage surges. The suppressor shall utilize thermally protected silicon-oxide varistors encapsulated in a non-conductive housing. Mechanical indicators shall be provided on each phase to indicate protection has been lost. The suppressor shall have a surge current rating of 100,000 amps per phase and a 100kA interrupting rating.

    - Voltage Alert Indication

      - The control panel shall include a voltage alert indicator to reduce the risk of electrical arc flash by pre-verifying the electrical isolation from outside of the control panel. Hardwired to the main incoming point of termination, the indicator shall be powered by the same voltage that it indicates utilizing redundant circuitry, thereby flashing whenever voltage is present. An eight (8) detector display shall visually alert the presence of dangerous AC or DC potentials occurring between any combinations of the monitored input lines.

    - Pump Start Delay

      - The control circuit for pump #2 shall be equipped with a time delay to prevent simultaneous motor starts.

    - Panel Heater

      - The control panel shall be equipped with a panel heater to minimize the effects of humidity and condensation. The heater shall include a thermostat.

  - CONTROL CIRCUIT

    - A normal duty thermal-magnetic circuit breaker shall protect all control circuits by interrupting control power.

    - Pump mode selector switches shall permit manual start or stop of each pump individually or permit automatic operation under control of the liquid level control system. Manual operation shall override all shutdown systems, except the motor overload relays. Selector switches are to be oil-tight design with contacts rated NEMA A300 minimum.

    - Pump alternation shall be integral to the liquid level controller. Provisions for automatic alternation or manual selection shall also be integral to the liquid level controller.

    - Six (6) digit elapsed time meter (non-reset type) shall be connected to each motor starter to indicate total running time of each pump in "hours" and "tenths of hours". An integral pilot light shall be wired in parallel to indicate that the motor is energized and should be running.

    - A high pump temperature protection circuit shall override the level control and shut down the pump motor(s) when required to protect the pump from excessive temperature. A thermostat shall be mounted on each pump casing and connected to a pump shutdown circuit. If casing temperature rises to a level sufficient to cause damage, the thermostat causes the shutdown circuit to interrupt power to the motor. A visible indicator, mounted through the control panel door shall indicate motor has stopped due to high pump temperature. The motor shall remain locked out until the pump has cooled and circuit has been manually reset. Automatic reset of this circuit is not acceptable.

    - A duplex ground fault receptacle providing 115 VAC, 60 Hz, single phase current, will be mounted on the side of the control enclosure. Receptacle circuit shall be protected by a 15 amp thermal-magnetic circuit breaker.

    - Auxiliary Power Transformer

      - The lift station shall be equipped with a five (5) KVA step-down transformer to supply 115 volt, AC, single phase for the control and auxiliary equipment. The primary and secondary side of the transformer is to be protected by a thermal magnetic circuit breaker, sized to meet the power requirements of the transformer. An operating mechanism shall penetrate the control panel door, and a padlockable operator handle shall be secured on the exterior surface. Interlocks must prevent opening the door until circuit breakers are in "OFF" position. An additional mechanism(s) shall be provided on the circuit breaker permitting the breaker to be operated and/or locked with the control panel door in the open position.

    - Wiring

      - The pump station, as furnished by the manufacturer, shall be completely wired, except for power feed lines to the branch circuit breakers and final connections to SCADA system RTU alarm and equipment status  monitoring devices.

      - All wiring, workmanship, and schematic wiring diagrams shall comply with applicable standards and specifications of the National Electric Code (NEC).

      - All user serviceable wiring shall be type MTW or THW, 600 volts, color coded as follows:

        - Line and Load Circuits, AC or DC power................................Black

        - AC Control Circuit Less Than Line Voltage...............................Red

        - DC Control Circuit.....................................................................Blue

        - Interlock Control Circuit, from External Source……............Yellow

        - Equipment Grounding Conductor............................................Green

        - Current Carrying Ground.........................................................White

        - Hot With Circuit Breaker Open.............................................Orange

      - Control circuit wiring inside the panel, with exception of internal wiring of individual components, shall be 16 gauge minimum, type MTW or THW, 600 volts. Power wiring to be 14 gauge minimum. Motor branch wiring shall be 10 gauge minimum.

      - Motor branch and other power conductors shall not be loaded above the temperature rating of the connected termination. Wires must be clearly numbered at each end in conformance with applicable standards. All wire connectors in the control panel shall be ring tongue type with nylon insulated shanks. All wires on the sub-plate shall be bundled and tied. All wires extending from components mounted on the door shall terminate at a terminal block mounted on the back panel. All wiring outside the panel shall be routed through conduit.

      - Control wires connected to door mounted components must be tied and bundled in accordance with good commercial practice. Bundles shall be made flexible at the hinged side of the enclosure. Adequate length and flex shall allow the door to swing full open without undue stress or abrasion. Bundles shall be held on each side of hinge by mechanical fastening devices.

    - Conduit

      - Factory installed conduit shall conform to following requirements:

        - All conduit and fittings to be UL listed.

        - Liquid tight flexible metal conduit to be constructed of smooth, flexible galvanized steel core with smooth abrasion resistant, liquid tight polyvinyl chloride cover.

        - Conduit to be supported in accordance with articles 346, 347, and 350 of the National Electric Code.

        - Conduit shall be sized according to the National Electric Code.

    - Grounding

      - Station manufacturer shall ground all electrical equipment inside the pump station to the control panel back plate. All paint must be removed from the grounding mounting surface before making final connection.

      - The contractor shall provide an earth driven ground connection to the pump station at the main grounding lug in accordance with the National Electric Code (NEC).

    - Equipment Marking

      - Permanent corrosion resistant name plate(s) shall be attached to the control and include following information:

        - Equipment serial number

        - Control panel short circuit rating

        - Supply voltage, phase and frequency

        - Current rating of the minimum main conductor

        - Electrical wiring diagram number

        - Motor horsepower and full load current

        - Motor overload heater element

        - Motor circuit breaker trip current rating

        - Name and location of equipment manufacturer

      - Control components shall be permanently marked using the same identification keys shown on the electrical diagram. Labels shall be mounted adjacent to device being identified.

      - Switches, indicators, and instruments mounted through the control panel door shall be labeled to indicate function, position, etc.  Labels shall be mounted adjacent to or above the device.

  - LIQUID LEVEL CONTROL

    - The manufacturer of the liquid level control system must be ISO 9001:2000 revision certified, with scope of registration including design control and service after sales activities.

    - The level control system shall start and stop the pump motors in response to changes in wet well level, as set forth herein.

    - The level control system shall be capable of operating as either an air bubbler type level control system or ultrasonic transmitter type system.

    - The level control system shall utilize alternation to select first one (1) pump, then the second pump, to run as lead pump for a pumping cycle.  Alternation shall occur at the end of a pumping cycle, or in the event of excessive run time.

    - The level control system shall utilize an electronic pressure switch which shall continuously monitor the wet well level, permitting the operator to read wet well level at any time.  Upon operator selection of automatic operation, the electronic pressure switch shall start the motor for one (1) pump when the liquid level in the wet well rises to the "lead pump start level".  When the liquid is lowered to the "lead pump stop level", the electronic pressure switch shall stop this pump. These actions shall constitute one (1) pumping cycle. Should the wet well level continue to rise, the electronic pressure switch shall start the second when the liquid reaches the "lag pump start level", or “standby pump start level” so that all pumps are operating. These levels shall be adjustable as described below.

    - The electronic pressure switch shall include integral components to perform all pressure sensing, signal conditioning, EMI and RFI suppression, DC power supply and 120 volt outputs. Comparators shall be solid state and shall be integrated with other components to perform as described below.

    - The electronic pressure switch shall be capable of operating on a supply voltage of 12VDC in an ambient temperature range of -10 degrees C (14 degrees F) through 55 degrees C (131 degrees F). Control range shall be zero to 12 feet of water with an overall repeat accuracy of (plus/minus) 0.1 feet of water. Memory shall be non-volatile.

    - The electronic pressure switch shall consist of the following integral components: pressure sensor, display, electronic comparators and output relays.

      - The internal pressure sensor shall be a strain gauge transducer and shall receive an input pressure from the air bubbler system. The transducer shall convert the input to a proportional electrical signal for distribution to the display and electronic comparators.  The transducer output shall be filtered to prevent control response to level pulsations or surges.  The transducer range shall be 0-15 PSI, temperature compensated from -40 degrees C (-40 degrees F) through 85 degrees C (185 degrees F), with a repeat accuracy of (plus/minus) 0.25% full scale about a fixed temperature. Transducer overpressure rating shall be three (3) times full scale.

      - The electronic pressure switch shall incorporate a digital back lighted LCD panel display which, upon operator selection, shall indicate liquid level in the wet well, and the preset start and stop level for both lead and lag pump. The display shall include 20, 0.19" high alpha-numeric characters calibrated to read out directly in feet of water, accurate to within one-tenth foot (0.1 foot), with a full scale indication of not less than 12 feet. The display shall be easily convertible to indicate English or metric units.

      - Level adjustments shall be electronic comparator set-points to control the levels at which the lead and lag pumps start and stop. Each of the level settings shall be easily adjustable with the use of membrane type switches, and accessible to the operator without opening any cover panel on the electronic pressure switch. Controls shall be provided to permit the operator to read the selected levels on the display. Such adjustments shall not require hard wiring, the use of electronic test equipment, artificial level simulation or introduction of pressure to the electronic pressure switch.

      - Each output relay in the electronic pressure switch shall be solid state.  Each relay input shall be optically isolated from its output and shall incorporate zero crossover switching to provide high immunity to electrical noise.  The "ON" state of each relay shall be indicated by illumination of a light emitting diode.  The output of each relay shall be individually fused providing overload and short circuit protection.  Each output relay shall have an inductive load rating equivalent to one (1) NEMA size four (4) contactor.  A pilot relay shall be incorporated for loads greater than a size four (4) contactor.

    - The electronic pressure switch shall be equipped with an output board which shall include LED status indicators and a connector with cable for connection to the main unit.

    - The electronic pressure switch shall be equipped with pump start delay(s) preset at a fixed delay time of five (5) seconds.

    - Circuit design in which application of power to the lag pump motor starter is contingent upon completion of the lead pump circuit shall not be acceptable.

    - The electronic pressure switch shall be equipped with a simulator system capable of performing system cycle testing functions.

    - The electronic pressure switch shall be capable of controlling liquid levels in either a pump up or pump down application.

    - The electronic pressure switch shall have internal capability of providing automatic alternation, manual selection of pump sequence operation and alternation in the event of 1-199 hours excessive run time.

    - The electronic pressure switch shall be equipped with a security access code to prevent accidental set-up changes and provide liquid level set-point lock-out.

    - The electronic pressure switch shall be equipped with one (1) 0-33 ft. W.C. input, one (1) scalable analog input of either 0-5VDC, 0-10VDC, or 4-20mA, and one (1) 4-20mA scalable output. Output is powered by 10-24VDC supply.  Load resistance for 4-20mA output shall be 100-1000 ohms.

    - The electronic pressure switch shall include a DC power supply to convert 120VAC control power to 12 or 24VDC EPS power. The power supply shall be 500 mA (6W) minimum and be UL listed Class II power limited power supply.

    - The electronic pressure switch shall be equipped with an electronic comparator and solid state output relay to alert maintenance personnel to a high liquid level in the wet well. An indicator, visible on the front of the control panel, shall indicate that a high wet well level exists.  The alarm signal shall be maintained until the wet well level has been lowered and the circuit has been manually reset. High water alarm shall be furnished with a dry contact wired to terminal blocks.

    - The electronic pressure switch shall be equipped with an electronic comparator and solid state output relay to alert maintenance personnel to a low liquid level in the wet well. An indicator, visible on the front of the control panel, shall indicate that a low wet well level exists. The alarm signal shall be maintained until the cause for the low wet well level has been corrected and the circuit has been manually reset. A low liquid level condition shall disable both pump motors. When the wet well rises above the low level point, both pump motors shall be automatically enabled. Low water alarm shall be furnished with a dry contact wired to terminal blocks.

    - EPS Analog Output circuit will be furnished with transient voltage surge suppression to protect related equipment from induced voltage spike from lighting.

    - An alarm silence pushbutton and relay shall be provided to permit maintenance personnel to de-energize the audible alarm device while corrective actions are under way. After silencing the alarm device, manual reset of the alarm condition shall clear the alarm silence relay automatically. The pushbutton shall be oil tight design with contacts rated NEMA A300 minimum.

  - AIR BUBBLER SYSTEM

    - The level control system shall be the air bubbler type, containing air bubbler piping which extends into the wet well. A pressure sensor contained within the electronic pressure switch shall sense the air pressure in this piping to provide wet well level signals for the remainder of the level control system.

    - Two (2) vibrating reed, industrial rated, air pumps shall be furnished to deliver free air at a rate of approximately five (5) cubic feet per hour and a pressure not to exceed seven (7) psi.  Liquid level control systems utilizing air compressors delivering greater quantities of air at higher pressures, requiring pressure reducing valves air storage reservoirs and other maintenance nuisance items will not be acceptable. A selector switch shall be furnished to provide manual alternation of the air pumps. The switch shall be connected in such a manner that either pump may be selected to operate continuously. The selector switch shall be oil tight design with contacts rated NEMA A300 minimum.

    - An air bell constructed of PVC three (3) inches in diameter shall be provided for installation at the outlet of the air bubbler line in the wet well. The air bell shall have a 3/8 inch NPT tapped fitting for connection to the bubbler line.

    - An air flow indicator gauge shall be provided and connected to the air bubbler piping to provide a visual indication of rate of flow in standard cubic feet per hour.

  - ALARM LIGHT (EXTERNAL)

    - Station manufacturer will supply one (1) 115 VAC alarm light fixture with vapor-tight shatter resistant red globe, conduit box, and mounting base. The design must prevent rain water from collecting in the gasketed area of the fixture, between the base and globe. The alarm light will be shipped loose for installation by the contractor.

  - ANTI-SEPTIC TIMER CIRCUIT

    - A 0-30 hour field adjustable Anti-Septic timer circuit shall interface with the pump level control to operate the lead pump until “Pump Off” level is reached. Timer circuit will reset after each cycle to reduce potential of sewage turning septic in the wet well during low flow periods.

- EXECUTION

  - PUMP TEST

    - The pump manufacturer shall perform the following inspections and tests on each pump before shipment from factory:

    - Impeller, motor rating and electrical connections shall first be checked for compliance to the customer's purchase order.

    - A motor and cable insulation test for moisture content or insulation defects shall be performed.

    - Prior to submergence, the pump shall be operated dry to establish correct rotation and mechanical integrity.

    - The pump shall be test-operated for 30 minutes submerged, a minimum of six (6) feet under water.

    - After operational test D., the insulation test (B.) shall be performed again.

    - A certified written report stating the foregoing steps have been done shall be supplied with each pump at the time of shipment. The report shall also provide the results of the operational test and note any deficiencies detected and/or repaired.

  - INSTALLATION AND OPERATING INSTRUCTIONS

    - Installation of pumping unit and unrelated appurtenances shall be done in accordance with written instructions provided by the manufacturer.

  - MANUFACTURER’S REPRESENTATIVE

    - A manufacturer's representative must be on the site during installation, startup, and testing. Provide representative a minimum of one (1) day. Site visits and time at the site above these minimums shall be provided if necessary to satisfactorily startup the equipment at no additional cost to the Owner.

  - PUMP WARRANTY

    - The pump manufacturer shall warrant the units being supplied to the Owner against defects in workmanship and material for a period of five (5) years or 10,000 hours under normal use, operation and service. The warranty shall be in printed form and apply to all similar units.

END OF SECTION