## WATER
WISE COUNTY PUBLIC SERVICE AUTHORITY - APPROVED MATERIALS LIST - WATER SYSTEMS
ITEM | ACCEPTABLE MANUFACTURERS | Model Number(s), when applicable | SPECIAL NOTES/CONDITIONS
Main Line Pipe - PVC - C900 |  |  | C900 only - C909 is specifically prohibited - DR-25 is specifically prohibited
DR-18, Cl 150 | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used only up to 150 psi maximum pressure from 4" to 12"
DR-14, Cl 200, DIOD | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used only up to 200 psi maximum pressure from 4" to 12"
Main Line Pipe - PVC - Sch 80 | Charlotte Pipe, others as equivalent |  | For sizes smaller than 4", up to 350 psi
Main Line Pipe - HDPE - C906 |  |  | All sizes less than DR-11 are specifically prohibited
DR-11, Cl 150, DIOD | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 150 psi maximum pressure from 4" to 12"
DR-9, Cl 200, DIOD | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 200 psi maximum pressure from 4" to 12"
DR-7, Cl 250 | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 250 psi maximum pressure from 4" to 12"
Main Line Pipe - HDPE - C901
SDR-9, CTS | Endot Industries |  | For sizes smaller than 4", up to 200 psi
Main Line Pipe - Ductile Iron |  |  | Mechanical & Slip joints only
Class 50 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | To be used up to 350 psi maximum
Class 51 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent
Class 52 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | Min class for flanged pipe
Class 53 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent
Class 54 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent
Class 55 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent
Class 56 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent
Gate Valves (including tapping valves) | American-Darling, Clow, M&H, Kennedy, Mueller, others as equivalent |  | Resilient Wedge only, no double disc gates allowed, up to 14" only
Butterfly Valves | American-Darling, Dresser, Pratt, others as equivalent |  | For 16" & larger
Valve Boxes | Tyler, others as equivalent | 6850 with 5-1/4" drop lid
Fire Hydrants | Mueller | A-423 Super Centurion | 5-1/4" main valve opening with 2 hose and 1 pumper nozzles
| Kennedy | K-81-A Guardian
| American Darling | B-84-B-5
Meter Setters
3/4" Single | Ford | VBH72-7W-44-33-G | No exceptions allowed under any circumstances
3/4" Tandem | Ford | TVBH72-9W-44-33-G | No exceptions allowed under any circumstances
1" Single | Ford | VBH74-10W-44-44-G | No exceptions allowed under any circumstances
1" Tandem | Ford | TVBH74-15W-44-44-G | No exceptions allowed under any circumstances
2" | Ford | VBH77-12-11-77-NL | Use for both 1-1/2" and 2" meters. Use adapters for installation of 1-1/2" meters. No exceptions allowed under any circumstances
Meters
3/4" - 1" | Sensus | iPERL | No exceptions allowed under any circumstances
1-1/2" - 2" | Sensus | Omni | Compound or Turbo - type to be determined by PSA for particular application - no exceptions under any circumstances
3" & above | Sensus | Omni | Compound or Turbo - type to be determined by PSA for particular application - no exceptions under any circumstances
Corporation Stops | Ford, others as equivalent | F10003GNL for 3/4", F10004GNL for 1"
Service Line Fittings
Couplings | Ford, others as equivalent | C4433GNL for 3/4", C4444GNL for 1", C4477GNL for 2"
Male Adapters | Ford, others as equivalent | C8433GNL for 3/4", C8444GNL for 1", C8477GNL for 2"
Female Adapters | Ford, others as equivalent | C1433GNL for 3/4", C1444GNL for 1", C1477GNL for 2"
Tees | Ford, others as equivalent | T444333GNL for 3/4", T444444GNL for 1", T444777GNL for 2"
Bends | Ford, others as equivalent | L4433GNL for 3/4", L4444GNL for 1", L4477GNL for 2"
Curb Stops (grip joint) | Ford, others as equivalent | B44333GNL for 3/4", B44444GNL for 1", B44777GNL for 2"
Curb Stops (female iron pipe) |  | B11333NL for 3/4", B11444NL for 1", B11777NL for 2"
Tapping Sleeves
For PVC or DI Pipe | Mueller, others as equivalent | H304DI | Stainless only, 4" to 12", up to 250 psi working pressure - 14" & larger to be project specific
For HDPE Pipe | Romac, others as equivalent | SST-H | Stainless only, 4" to 12", up to 250 psi working pressure
Fittings | DI pipe manufacturers above, Tyler Union, Sigma, Star Pipe, others as equivalent |  | All fittings to be ductile iron, no PVC fittings allowed. MJ fittings may be compact (AWWA C153) or full size (AWWA C110). Flanged fittings to be AWWA C110, flange rating to specificed on project basis.
90 deg bends
45 deg bends
22.5 deg bends
11.25 deg bends
Tees
Crosses
Reducers
Solid Sleeve Couplings |  |  | MJ Solid Sleeve type couplings to be "long" type
Restrained Couplings | Romac | Alpha
| EBAA Iron | Series 3800
| Hymax | Grip
others as equivalent
Air Release Only Valves | ARI | S-050 for sizes less than 2", D-060/062 for sizes 2" & larger | No exceptions allowed
Air Combination Valves | ARI | D-060/062 for all sizes | No exceptions allowed
Flushing Hydrants/Blow Offs | Kupferle M78
| others as equivalent |  | Other manufacturers must demonstrate that their products can be locked against unauthorized use
Water Meter Boxes
3/4" and 1" Single Setter | Carson | Model 1520
3/4" Tandem Setter | Carson | Model 0024-B
1" Tandem Setter | Carson | Model 0030-B
3/4" Tandem Setter Covers | Vestal | Model RMC20L-W/SN-W/TR Lid, Model ER-2024 Expander
1" Tandem Setter Covers | Vestal | Model RMC20L-W/SN-W/TR Lid, Model ER-2030 Expander
1-1/2" and 2" Meters | Carson | Model 1730BCF
others as equivalent
Service Line Tubing
3/4" - 1" HDPE CTS SDR 9 | Endot Industries | Endopure | Use only up to 200 psi
3/4" - 1" Copper - Type K malleable |  |  | Use for above 200 psi
2" HDPE CTS SDR 9 | Endot Industries |  | Use only up to 200 psi
2" Copper - Type K malleable |  |  | Use for above 200 psi
others as equivalent
Service Tapping Saddles | Ford
For non-C900 PVC | Ford | S70 for smaller than 2" service, S71 for 2" service; all design A
For C900 PVC | Ford | S90 for smaller than 2" service, S91 for 2" service; design A for 4"-8", design B for 10" & 12"
For DI and HDPE | Ford | FSD202 for all ductile sizes
Universal | TPS | T3 for 4" to 30" pipe and 1/2" to 2" service lines
others as equivalent
Pipe Joint Restraints |  |  | This is for external joint restraints - integral joint restraints are acceptable
For C900 PVC (4"-12") | Romac | PVC Romagrip - for MJ fitting joint restraint | other restraint systems, such as GripRing, will be considered
| Romac | 600 Series - for in-line joint restraint
| EBAA Iron | Series 2000PV
For DI (4" & above") | Romac | Romagrip - for MJ fitting joint restraint | other restraint systems, such as GripRing, will be considered
| EBAA Iron | Series 1100 or 1100 TDM | model to depend on working pressure
others as equivalent
Line Detection Markers | Omni | blue for water
others as equivalent
Tandem Setter PRV's - 3/4" and 1" | Zurn-Wilkins | 600XL
| others as equivalent |  | must be rated for 300 psi inlet pressure
PRV's - 1-1/2" and 2" Meters | Zurn-Wilkins | 600XL
| others as equivalent |  | must be rated for 300 psi inlet pressure
Main Line Control Valves (PRV's, FCV, PSV's, etc.) |  |  | no manufacturer exceptions allowed
| Cla-Val | model type to depend on application - consult with factory rep and PSA staff
| Bermad | model type to depend on application - consult with factory rep and PSA staff
Reduced Pressure Zone Backflow Preventer | Watts Regulator | LF009 (established as standard - other models may be considered on case-by-case basis)
others as equivalent

## SEWER
WISE COUNTY PUBLIC SERVICE AUTHORITY - APPROVED MATERIALS LIST - SEWER SYSTEMS
ITEM | ACCEPTABLE MANUFACTURERS | Model Number(s), when applicable | SPECIAL NOTES/CONDITIONS
Main Line Gravity Pipe - PVC
SDR-35 Solid Wall (4" to 15") | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used for gravity sewer applications only - ductile iron or pressure rated PVC may be required in particular situations
PS-46 Solid Wall (18" to 48") | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used for gravity sewer applications only - ductile iron or pressure rated PVC may be required in particular situations
Main Line Gravity Pipe - Ductile Iron
Pressure Class 350 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 50 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 51 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 52 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 53 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 54 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 55 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Thickness Class 56 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Main Line Forcemain or Gravity Pipe - PVC - C900 |  |  | C900 only - C909 is specifically prohibited - DR-25 is specifically prohibited
DR-18, Cl 150 | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used only up to 150 psi maximum pressure from 4" to 12" - may be required for use in some gravity sewer applications
DR-14, Cl 200 | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent |  | To be used only up to 200 psi maximum pressure from 4" to 12"
Main Line Forcemain Pipe - PVC - Sch 80 | Charlotte Pipe, others as equivalent |  | For sizes 2" & smaller
Main Line Forcemain Pipe - HDPE - C906 |  |  | All sizes less than DR-11 are specifically prohibited
DR-11, Cl 150, DIOD - DIPS | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 150 psi maximum pressure from 4" to 12"
DR-9, Cl 200, DIOD - DIPS | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 200 psi maximum pressure from 4" to 12"
DR-7, Cl 250 - DIPS | JM Eagle, Performance Pipe, others as equivalent |  | To be used only up to 250 psi maximum pressure from 4" to 12"
Main Line Pipe - HDPE - C901
SDR-9, CTS | Endot Industries |  | For sizes 2" & smaller, up to 200 psi
Main Line Forcemain Pipe - Ductile Iron
Class 50 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | To be used up to 350 psi maximum pressure for MJ & Slip Joint only. All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 51 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 52 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | Min class for flanged pipe. All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 53 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 54 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 55 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Class 56 | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Manholes | Oldcastle Precast, others as equivalent
Manhole Frames & Covers
Standard | East Jordan Iron Works | R-1642-G | in all paved areas not subject to flooding
Watertight | East Jordan Iron Works | R-1642-G | only in floodplains or flood prone areas - must include hold-down bar and rubber gasketed inner cover per details
Neenah or US Foundry are acceptable
Cleanout Boxes & Covers | Neenah | R-1975-A2 | must have "SEWER" on lid
others as equivalvent
Lateral Taps | Inserta-Tee Company | Inserta-Tee
| Romac | CB Sewer Saddle
others as equivalvent
Lateral Pipe & Service Fittings - PVC |  |  | for 4" & 6" laterals
Pipe - SDR 35 | JM Eagle, IPEX, Diamond Plastics, National Pipe, others as equivalent
Fittings - SDR 35 | Multi-Fittings, others as equivalent
Lateral Pipe & Service Fittings - Ductile Iron
Pipe | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Fittings | American Cast Iron Pipe Co, US Pipe, McWane Ductile, others as equivalent |  | All ductile iron pipe for use in sewer systems is to have the cement lining replaced with Series 431 Perma-Sheild PL - no exceptions
Forcemain Plug Valves | Pratt, DeZurik, or Millken |  | 100% port area
Valve Boxes | Tyler, others as equivalent | 6850 with 5-1/4" drop lid
Air Combination Valves | ARI | D-020 or D-023 | no exceptions allowed
Manhole Adjustment Rings | Concrete or Polymer
Pipe Joint Restraints |  |  | This is for external joint restraints - integral joint restraints are acceptable
For C900 PVC (4"-12") | Romac | PVC Romagrip - for MJ fitting joint restraint | other restraint systems, such as GripRing, will be considered
| Romac | 600 Series - for in-line joint restraint
others as equivalent
For DI (4" & above") | Romac | Romagrip - for MJ fitting joint restraint | other restraint systems, such as GripRing, will be considered
others as equivalent
Line Detection Markers | Omni | green for sewer
others as equivalent
Note on D9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Update to new product used for jetting, TNEMEC brand/model PermaShield Series 431
Note on D60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TNEMEC PermaShield here no 401